## plant_metadata
Parameter | Value
plant_id | SPV_ALPHA_01
plant_name | Alpha Solar Power Plant
ac_capacity_kw | 115000
dc_capacity_kwp | 135000
num_inverters | 12
inverter_capacity_kw | 9583.3
location | Sample Location, India
commissioning_date | 2022-01-01
data_interval_minutes | 5
pr_target_percent | 75
cuf_target_percent | 22
module_efficiency_percent | 20.5
pv_area_m2 | 658536
currency | INR
reporting_timezone | IST (UTC+5:30)

## daily_kpis
date | plant_id | ac_capacity_kw | dc_capacity_kwp | generation_kwh | gti_kwh_m2 | pr_percent | cuf_percent | expected_generation_kwh | total_loss_kwh | outage_loss_kwh | environmental_loss_kwh | clipping_loss_kwh | data_availability_percent | peak_power_kw | sunshine_hours | prev_day_generation_kwh | prev_day_pr_percent
2025-06-01 | SPV_ALPHA_01 | 115000 | 135000 | 534400 | 5.62 | 74.1 | 19.36 | 667656 | 133256 | 26651 | 66628 | 39977 | 98.2 | 105330 | 8.48 | 534400 | 74.1
2025-06-02 | SPV_ALPHA_01 | 115000 | 135000 | 612300 | 5.76 | 82.9 | 22.18 | 684288 | 71988 | 14398 | 35994 | 21596 | 99.2 | 98150 | 10.05 | 534400 | 74.1
2025-06-03 | SPV_ALPHA_01 | 115000 | 135000 | 538400 | 5.62 | 74.7 | 19.51 | 667656 | 129256 | 25851 | 64628 | 38777 | 98.6 | 109690 | 8.59 | 612300 | 82.9
2025-06-04 | SPV_ALPHA_01 | 115000 | 135000 | 390400 | 3.56 | 85.6 | 14.14 | 422928 | 32528 | 3253 | 26022 | 3253 | 98.8 | 94814 | 5.6 | 538400 | 74.7
2025-06-05 | SPV_ALPHA_01 | 115000 | 135000 | 610800 | 7.24 | 65.8 | 22.13 | 860112 | 249312 | 49862 | 124656 | 74794 | 99.1 | 94758 | 11.34 | 390400 | 85.6
2025-06-06 | SPV_ALPHA_01 | 115000 | 135000 | 633600 | 6.64 | 74.2 | 22.96 | 788832 | 155232 | 31046 | 77616 | 46570 | 99 | 103700 | 10.45 | 610800 | 65.8
2025-06-07 | SPV_ALPHA_01 | 115000 | 135000 | 656900 | 6.77 | 75.3 | 23.8 | 804276 | 147376 | 29475 | 73688 | 44213 | 99.5 | 108263 | 10.17 | 633600 | 74.2
2025-06-08 | SPV_ALPHA_01 | 115000 | 135000 | 639500 | 6.64 | 74.8 | 23.17 | 788832 | 149332 | 29866 | 74666 | 44800 | 97.9 | 106343 | 10.71 | 656900 | 75.3
2025-06-09 | SPV_ALPHA_01 | 115000 | 135000 | 647700 | 7.22 | 69.7 | 23.47 | 857736 | 210036 | 42007 | 105018 | 63011 | 97.7 | 110812 | 11.64 | 639500 | 74.8
2025-06-10 | SPV_ALPHA_01 | 115000 | 135000 | 569800 | 6.39 | 69.2 | 20.64 | 759132 | 189332 | 37866 | 94666 | 56800 | 99 | 95968 | 11.39 | 647700 | 69.7
2025-06-11 | SPV_ALPHA_01 | 115000 | 135000 | 494600 | 5.83 | 66 | 17.92 | 692604 | 198004 | 39601 | 99002 | 59401 | 98.8 | 108223 | 10.16 | 569800 | 69.2
2025-06-12 | SPV_ALPHA_01 | 115000 | 135000 | 378500 | 4.61 | 63.8 | 13.71 | 547668 | 169168 | 33834 | 84584 | 50750 | 98.9 | 111086 | 7.5 | 494600 | 66
2025-06-13 | SPV_ALPHA_01 | 115000 | 135000 | 444700 | 5.09 | 68.1 | 16.11 | 604692 | 159992 | 31998 | 79996 | 47998 | 99.7 | 108607 | 8.68 | 378500 | 63.8
2025-06-14 | SPV_ALPHA_01 | 115000 | 135000 | 513700 | 7.49 | 50.88 | 18.61 | 889812 | 376112 | 282084 | 56417 | 37611 | 97.6 | 104259 | 12.99 | 444700 | 68.1

## daily_timeseries
timestamp | plant_id | inv_power_kw | gti_wm2 | temperature_c | wind_speed_ms | freq_hz
2025-06-14 05:00:00 | SPV_ALPHA_01 | 0 | 0 | 27.5 | 2.4 | 49.96
2025-06-14 05:05:00 | SPV_ALPHA_01 | 0 | 0 | 27.5 | 1.8 | 49.98
2025-06-14 05:10:00 | SPV_ALPHA_01 | 0 | 0 | 28.3 | 2.6 | 49.99
2025-06-14 05:15:00 | SPV_ALPHA_01 | 0 | 0 | 27.4 | 2.3 | 50.04
2025-06-14 05:20:00 | SPV_ALPHA_01 | 0 | 0 | 28.3 | 3.3 | 49.97
2025-06-14 05:25:00 | SPV_ALPHA_01 | 0 | 0 | 28.5 | 2 | 49.99
2025-06-14 05:30:00 | SPV_ALPHA_01 | 0 | 0 | 29 | 3.4 | 50.01
2025-06-14 05:35:00 | SPV_ALPHA_01 | 0 | 0 | 28.4 | 4 | 50.03
2025-06-14 05:40:00 | SPV_ALPHA_01 | 0 | 0 | 27.5 | 1.6 | 49.98
2025-06-14 05:45:00 | SPV_ALPHA_01 | 0 | 0 | 28.9 | 4.1 | 49.98
2025-06-14 05:50:00 | SPV_ALPHA_01 | 2069 | 16.7 | 29.1 | 2.9 | 49.98
2025-06-14 05:55:00 | SPV_ALPHA_01 | 4041 | 32.1 | 28.1 | 3.3 | 50.04
2025-06-14 06:00:00 | SPV_ALPHA_01 | 5953 | 48.9 | 29.9 | 3 | 49.96
2025-06-14 06:05:00 | SPV_ALPHA_01 | 7573 | 62.9 | 29.4 | 3.9 | 49.99
2025-06-14 06:10:00 | SPV_ALPHA_01 | 9736 | 78.7 | 30.4 | 3.1 | 50.05
2025-06-14 06:15:00 | SPV_ALPHA_01 | 12182 | 102.2 | 30.3 | 3.5 | 50
2025-06-14 06:20:00 | SPV_ALPHA_01 | 14247 | 112.3 | 29.2 | 2.8 | 50
2025-06-14 06:25:00 | SPV_ALPHA_01 | 17811 | 137.3 | 30 | 3 | 49.97
2025-06-14 06:30:00 | SPV_ALPHA_01 | 19929 | 153.7 | 30.4 | 3.4 | 50.01
2025-06-14 06:35:00 | SPV_ALPHA_01 | 20291 | 158.1 | 30.9 | 3.8 | 50
2025-06-14 06:40:00 | SPV_ALPHA_01 | 21034 | 171 | 30.1 | 4.3 | 50.04
2025-06-14 06:45:00 | SPV_ALPHA_01 | 24868 | 202.5 | 30.8 | 4.1 | 50.04
2025-06-14 06:50:00 | SPV_ALPHA_01 | 25395 | 203.2 | 30.8 | 3.8 | 50.03
2025-06-14 06:55:00 | SPV_ALPHA_01 | 27404 | 219.5 | 32.1 | 2.3 | 50.04
2025-06-14 07:00:00 | SPV_ALPHA_01 | 29424 | 241.9 | 32.4 | 3.7 | 49.97
2025-06-14 07:05:00 | SPV_ALPHA_01 | 33397 | 254.6 | 32.9 | 2.8 | 50
2025-06-14 07:10:00 | SPV_ALPHA_01 | 32239 | 264.7 | 32.4 | 3.3 | 49.97
2025-06-14 07:15:00 | SPV_ALPHA_01 | 33890 | 282.6 | 33.3 | 2.2 | 50.04
2025-06-14 07:20:00 | SPV_ALPHA_01 | 38039 | 317.2 | 33.2 | 3.5 | 49.97
2025-06-14 07:25:00 | SPV_ALPHA_01 | 40387 | 309.6 | 33.7 | 2.9 | 50.03
2025-06-14 07:30:00 | SPV_ALPHA_01 | 42118 | 347 | 33.4 | 2.8 | 49.99
2025-06-14 07:35:00 | SPV_ALPHA_01 | 44854 | 350.6 | 34.7 | 4.5 | 49.96
2025-06-14 07:40:00 | SPV_ALPHA_01 | 44730 | 363.1 | 35.3 | 2.2 | 49.97
2025-06-14 07:45:00 | SPV_ALPHA_01 | 47132 | 379.5 | 34.4 | 2.2 | 50.04
2025-06-14 07:50:00 | SPV_ALPHA_01 | 51029 | 393.9 | 35.2 | 1.7 | 50.05
2025-06-14 07:55:00 | SPV_ALPHA_01 | 55536 | 424.4 | 36.5 | 4 | 49.97
2025-06-14 08:00:00 | SPV_ALPHA_01 | 51633 | 424.4 | 35.4 | 1.7 | 49.99
2025-06-14 08:05:00 | SPV_ALPHA_01 | 56314 | 460.5 | 36.9 | 2.9 | 49.99
2025-06-14 08:10:00 | SPV_ALPHA_01 | 62179 | 474 | 36.6 | 3.7 | 49.97
2025-06-14 08:15:00 | SPV_ALPHA_01 | 59879 | 457.6 | 36.4 | 3.1 | 50.02
2025-06-14 08:20:00 | SPV_ALPHA_01 | 57976 | 459.5 | 36.3 | 4.1 | 49.97
2025-06-14 08:25:00 | SPV_ALPHA_01 | 62058 | 517 | 36.7 | 3.3 | 50.02
2025-06-14 08:30:00 | SPV_ALPHA_01 | 59548 | 494.1 | 37.7 | 2.2 | 50.01
2025-06-14 08:35:00 | SPV_ALPHA_01 | 65422 | 526.9 | 37.7 | 3.1 | 50.04
2025-06-14 08:40:00 | SPV_ALPHA_01 | 66177 | 517.9 | 36.8 | 2.7 | 50.02
2025-06-14 08:45:00 | SPV_ALPHA_01 | 65805 | 535.4 | 38.1 | 1.7 | 50
2025-06-14 08:50:00 | SPV_ALPHA_01 | 76981 | 586.8 | 37.7 | 2.1 | 49.98
2025-06-14 08:55:00 | SPV_ALPHA_01 | 77352 | 596 | 39.5 | 2.6 | 49.97
2025-06-14 09:00:00 | SPV_ALPHA_01 | 76933 | 602.8 | 39.1 | 4.5 | 50.02
2025-06-14 09:05:00 | SPV_ALPHA_01 | 73006 | 565.9 | 37.8 | 3.5 | 50.04
2025-06-14 09:10:00 | SPV_ALPHA_01 | 70423 | 584.6 | 37.7 | 3.2 | 49.98
2025-06-14 09:15:00 | SPV_ALPHA_01 | 79835 | 624.7 | 38.7 | 3.4 | 49.98
2025-06-14 09:20:00 | SPV_ALPHA_01 | 81783 | 628.7 | 40 | 1.8 | 49.99
2025-06-14 09:25:00 | SPV_ALPHA_01 | 74570 | 626.1 | 39.8 | 3.4 | 49.98
2025-06-14 09:30:00 | SPV_ALPHA_01 | 83868 | 666.8 | 39.9 | 1.5 | 49.96
2025-06-14 09:35:00 | SPV_ALPHA_01 | 89355 | 687 | 40.5 | 4 | 50.01
2025-06-14 09:40:00 | SPV_ALPHA_01 | 78180 | 648.2 | 39.3 | 4.2 | 50.03
2025-06-14 09:45:00 | SPV_ALPHA_01 | 91835 | 706.4 | 40.1 | 2.2 | 49.96
2025-06-14 09:50:00 | SPV_ALPHA_01 | 92292 | 710.9 | 40.6 | 3.4 | 49.97
2025-06-14 09:55:00 | SPV_ALPHA_01 | 94741 | 731.1 | 42.1 | 3.9 | 50.04
2025-06-14 10:00:00 | SPV_ALPHA_01 | 86598 | 676.4 | 39.8 | 4.3 | 50.03
2025-06-14 10:05:00 | SPV_ALPHA_01 | 96092 | 745.3 | 40.9 | 3.9 | 49.96
2025-06-14 10:10:00 | SPV_ALPHA_01 | 97757 | 754.8 | 41 | 3.9 | 50
2025-06-14 10:15:00 | SPV_ALPHA_01 | 92927 | 721.8 | 40.4 | 1.6 | 49.97
2025-06-14 10:20:00 | SPV_ALPHA_01 | 94777 | 731.4 | 42.1 | 2.3 | 50.01
2025-06-14 10:25:00 | SPV_ALPHA_01 | 97534 | 744.5 | 41.5 | 4.3 | 49.96
2025-06-14 10:30:00 | SPV_ALPHA_01 | 62774 | 480 | 36.2 | 1.8 | 49.99
2025-06-14 10:35:00 | SPV_ALPHA_01 | 63878 | 505.2 | 37.1 | 2.7 | 50.01
2025-06-14 10:40:00 | SPV_ALPHA_01 | 68542 | 575.6 | 39.2 | 3.1 | 50.02
2025-06-14 10:45:00 | SPV_ALPHA_01 | 74158 | 600.5 | 37.9 | 3.5 | 49.98
2025-06-14 10:50:00 | SPV_ALPHA_01 | 79404 | 621.2 | 38.8 | 2.4 | 49.99
2025-06-14 10:55:00 | SPV_ALPHA_01 | 60485 | 501.5 | 36.9 | 4.3 | 50.02
2025-06-14 11:00:00 | SPV_ALPHA_01 | 74910 | 610.4 | 39.1 | 1.5 | 49.98
2025-06-14 11:05:00 | SPV_ALPHA_01 | 73449 | 578.2 | 38.3 | 2.8 | 49.97
2025-06-14 11:10:00 | SPV_ALPHA_01 | 85259 | 662.2 | 39.3 | 1.8 | 50
2025-06-14 11:15:00 | SPV_ALPHA_01 | 69260 | 536.8 | 38.2 | 3.5 | 49.97
2025-06-14 11:20:00 | SPV_ALPHA_01 | 54015 | 442.6 | 35.9 | 4 | 49.96
2025-06-14 11:25:00 | SPV_ALPHA_01 | 73220 | 603 | 39.2 | 3 | 49.97
2025-06-14 11:30:00 | SPV_ALPHA_01 | 59409 | 463.4 | 36.9 | 1.8 | 49.99
2025-06-14 11:35:00 | SPV_ALPHA_01 | 105076 | 803.8 | 42.5 | 1.7 | 49.97
2025-06-14 11:40:00 | SPV_ALPHA_01 | 107557 | 863.1 | 44.1 | 3.5 | 50.05
2025-06-14 11:45:00 | SPV_ALPHA_01 | 110393 | 845.1 | 44 | 3.3 | 50.02
2025-06-14 11:50:00 | SPV_ALPHA_01 | 108531 | 840.2 | 43.2 | 4.2 | 50.02
2025-06-14 11:55:00 | SPV_ALPHA_01 | 102660 | 840 | 42.6 | 3.4 | 50.03
2025-06-14 12:00:00 | SPV_ALPHA_01 | 107193 | 846.1 | 42.8 | 1.7 | 49.98
2025-06-14 12:05:00 | SPV_ALPHA_01 | 101644 | 826.7 | 43 | 1.9 | 49.97
2025-06-14 12:10:00 | SPV_ALPHA_01 | 110286 | 863.9 | 42.7 | 2.7 | 50
2025-06-14 12:15:00 | SPV_ALPHA_01 | 102295 | 841.4 | 43 | 4.2 | 50.01
2025-06-14 12:20:00 | SPV_ALPHA_01 | 112139 | 866 | 44.1 | 2.6 | 49.95
2025-06-14 12:25:00 | SPV_ALPHA_01 | 107357 | 837.2 | 43.8 | 4.4 | 49.99
2025-06-14 12:30:00 | SPV_ALPHA_01 | 109492 | 871 | 43.9 | 2.2 | 49.97
2025-06-14 12:35:00 | SPV_ALPHA_01 | 100832 | 844.4 | 42.9 | 3.5 | 49.99
2025-06-14 12:40:00 | SPV_ALPHA_01 | 102407 | 820.9 | 42 | 3.4 | 49.95
2025-06-14 12:45:00 | SPV_ALPHA_01 | 105732 | 839.6 | 42.2 | 3.4 | 49.96
2025-06-14 12:50:00 | SPV_ALPHA_01 | 101026 | 844.2 | 43 | 2.1 | 49.98
2025-06-14 12:55:00 | SPV_ALPHA_01 | 107362 | 868.1 | 44.1 | 4 | 49.98
2025-06-14 13:00:00 | SPV_ALPHA_01 | 96510 | 809 | 42.6 | 4.5 | 49.98
2025-06-14 13:05:00 | SPV_ALPHA_01 | 109903 | 854.8 | 43.7 | 3.8 | 50.04
2025-06-14 13:10:00 | SPV_ALPHA_01 | 97176 | 814.5 | 42 | 1.9 | 50.02
2025-06-14 13:15:00 | SPV_ALPHA_01 | 102531 | 842.4 | 43.6 | 3.8 | 49.97
2025-06-14 13:20:00 | SPV_ALPHA_01 | 108044 | 843 | 42.4 | 4 | 50.05
2025-06-14 13:25:00 | SPV_ALPHA_01 | 95282 | 798.2 | 42 | 3.5 | 50.05
2025-06-14 13:30:00 | SPV_ALPHA_01 | 104576 | 818.5 | 41.9 | 3.6 | 50.01
2025-06-14 13:35:00 | SPV_ALPHA_01 | 101539 | 790.4 | 42.9 | 3.3 | 49.96
2025-06-14 13:40:00 | SPV_ALPHA_01 | 110393 | 858.5 | 43.1 | 2.8 | 49.99
2025-06-14 13:45:00 | SPV_ALPHA_01 | 100395 | 814.8 | 43.4 | 4 | 49.96
2025-06-14 13:50:00 | SPV_ALPHA_01 | 107360 | 846.7 | 43.9 | 3.6 | 49.99
2025-06-14 13:55:00 | SPV_ALPHA_01 | 107661 | 823 | 42.4 | 3.9 | 50
2025-06-14 14:00:00 | SPV_ALPHA_01 | 99167 | 797.4 | 42.8 | 2.3 | 50.04
2025-06-14 14:05:00 | SPV_ALPHA_01 | 98397 | 819.2 | 43.5 | 2.2 | 50
2025-06-14 14:10:00 | SPV_ALPHA_01 | 6231 | 795.5 | 41.4 | 4.1 | 49.97
2025-06-14 14:15:00 | SPV_ALPHA_01 | 10233 | 758 | 41.3 | 4.1 | 50.02
2025-06-14 14:20:00 | SPV_ALPHA_01 | 2151 | 756.5 | 42.5 | 1.8 | 50.02
2025-06-14 14:25:00 | SPV_ALPHA_01 | 9930 | 766 | 42.2 | 3.4 | 50
2025-06-14 14:30:00 | SPV_ALPHA_01 | 3100 | 781.8 | 41.5 | 3.6 | 49.98
2025-06-14 14:35:00 | SPV_ALPHA_01 | 6906 | 758.2 | 41.7 | 2.8 | 50.02
2025-06-14 14:40:00 | SPV_ALPHA_01 | 8937 | 731.6 | 40.7 | 2.3 | 49.96
2025-06-14 14:45:00 | SPV_ALPHA_01 | 3085 | 713.5 | 40.9 | 3.8 | 49.97
2025-06-14 14:50:00 | SPV_ALPHA_01 | 6545 | 707.1 | 41.2 | 4.4 | 50
2025-06-14 14:55:00 | SPV_ALPHA_01 | 2860 | 703.5 | 40.1 | 2.2 | 49.97
2025-06-14 15:00:00 | SPV_ALPHA_01 | 6711 | 675.7 | 39.7 | 4.4 | 50.01
2025-06-14 15:05:00 | SPV_ALPHA_01 | 3155 | 714.8 | 41.6 | 3 | 50.04
2025-06-14 15:10:00 | SPV_ALPHA_01 | 6309 | 696.6 | 40.4 | 2.1 | 49.96
2025-06-14 15:15:00 | SPV_ALPHA_01 | 6528 | 711.9 | 41.5 | 2.7 | 49.96
2025-06-14 15:20:00 | SPV_ALPHA_01 | 2335 | 680.5 | 39.5 | 3.2 | 49.98
2025-06-14 15:25:00 | SPV_ALPHA_01 | 2991 | 694.3 | 41 | 3.3 | 50.03
2025-06-14 15:30:00 | SPV_ALPHA_01 | 6191 | 633.3 | 39.3 | 2.8 | 50.04
2025-06-14 15:35:00 | SPV_ALPHA_01 | 4593 | 671.8 | 40.3 | 3.3 | 50.02
2025-06-14 15:40:00 | SPV_ALPHA_01 | 3628 | 657.6 | 39.3 | 3.5 | 49.97
2025-06-14 15:45:00 | SPV_ALPHA_01 | 2226 | 598.1 | 37.8 | 2.9 | 50.01
2025-06-14 15:50:00 | SPV_ALPHA_01 | 58374 | 594.2 | 39.1 | 2.9 | 50.02
2025-06-14 15:55:00 | SPV_ALPHA_01 | 63355 | 620.4 | 39.5 | 4.3 | 49.99
2025-06-14 16:00:00 | SPV_ALPHA_01 | 62199 | 585.9 | 39.2 | 1.7 | 49.97
2025-06-14 16:05:00 | SPV_ALPHA_01 | 56395 | 560.2 | 37.7 | 1.9 | 50.02
2025-06-14 16:10:00 | SPV_ALPHA_01 | 57680 | 570.1 | 38.2 | 1.7 | 49.95
2025-06-14 16:15:00 | SPV_ALPHA_01 | 49227 | 542.7 | 37 | 4.4 | 50.03
2025-06-14 16:20:00 | SPV_ALPHA_01 | 59702 | 537.7 | 38 | 2.3 | 49.95
2025-06-14 16:25:00 | SPV_ALPHA_01 | 53168 | 534.1 | 38.4 | 2 | 50.01
2025-06-14 16:30:00 | SPV_ALPHA_01 | 45907 | 514.4 | 37 | 2.5 | 50.02
2025-06-14 16:35:00 | SPV_ALPHA_01 | 50657 | 511.9 | 36.8 | 4.3 | 50.03
2025-06-14 16:40:00 | SPV_ALPHA_01 | 44984 | 483.2 | 36.3 | 4.4 | 49.99
2025-06-14 16:45:00 | SPV_ALPHA_01 | 48976 | 467.8 | 36.5 | 2.7 | 49.97
2025-06-14 16:50:00 | SPV_ALPHA_01 | 45515 | 447 | 36.6 | 2.1 | 50
2025-06-14 16:55:00 | SPV_ALPHA_01 | 45848 | 458 | 35.5 | 4.4 | 50.01
2025-06-14 17:00:00 | SPV_ALPHA_01 | 39192 | 413.9 | 35.6 | 1.8 | 50.05
2025-06-14 17:05:00 | SPV_ALPHA_01 | 53312 | 427.6 | 34.9 | 4 | 50
2025-06-14 17:10:00 | SPV_ALPHA_01 | 50691 | 404.7 | 34.8 | 4 | 50.05
2025-06-14 17:15:00 | SPV_ALPHA_01 | 46749 | 371.7 | 34.5 | 4.3 | 50
2025-06-14 17:20:00 | SPV_ALPHA_01 | 49318 | 380.6 | 34.4 | 3.9 | 49.99
2025-06-14 17:25:00 | SPV_ALPHA_01 | 45964 | 367 | 35.2 | 2.3 | 49.98
2025-06-14 17:30:00 | SPV_ALPHA_01 | 44563 | 339.6 | 34.1 | 1.9 | 50
2025-06-14 17:35:00 | SPV_ALPHA_01 | 39809 | 316.5 | 33.8 | 2.9 | 49.98
2025-06-14 17:40:00 | SPV_ALPHA_01 | 37832 | 296.6 | 33.5 | 2.2 | 50.03
2025-06-14 17:45:00 | SPV_ALPHA_01 | 35555 | 277.5 | 33.4 | 3.9 | 49.99
2025-06-14 17:50:00 | SPV_ALPHA_01 | 36096 | 279.7 | 34 | 3 | 49.95
2025-06-14 17:55:00 | SPV_ALPHA_01 | 32773 | 259.6 | 33.4 | 4.1 | 49.99
2025-06-14 18:00:00 | SPV_ALPHA_01 | 30458 | 244.4 | 32.8 | 2.7 | 50.02
2025-06-14 18:05:00 | SPV_ALPHA_01 | 27463 | 220.1 | 32.9 | 2.5 | 50.02
2025-06-14 18:10:00 | SPV_ALPHA_01 | 27853 | 215.2 | 32.6 | 4.1 | 49.99
2025-06-14 18:15:00 | SPV_ALPHA_01 | 24591 | 192.4 | 32 | 4.1 | 49.95
2025-06-14 18:20:00 | SPV_ALPHA_01 | 21825 | 172.2 | 31.9 | 4.5 | 50.02
2025-06-14 18:25:00 | SPV_ALPHA_01 | 19566 | 162.7 | 31.2 | 4.1 | 49.99
2025-06-14 18:30:00 | SPV_ALPHA_01 | 19574 | 150.5 | 29.8 | 3.9 | 49.98
2025-06-14 18:35:00 | SPV_ALPHA_01 | 15672 | 129.7 | 30.4 | 3.2 | 50.03
2025-06-14 18:40:00 | SPV_ALPHA_01 | 13346 | 111.2 | 30.7 | 3.4 | 49.97
2025-06-14 18:45:00 | SPV_ALPHA_01 | 12418 | 102.8 | 29.8 | 2.3 | 49.98
2025-06-14 18:50:00 | SPV_ALPHA_01 | 10089 | 78.3 | 30.2 | 3.5 | 49.97
2025-06-14 18:55:00 | SPV_ALPHA_01 | 8074 | 65.5 | 29.4 | 3.4 | 49.99
2025-06-14 19:00:00 | SPV_ALPHA_01 | 6235 | 48.2 | 28.3 | 2.7 | 50
2025-06-14 19:05:00 | SPV_ALPHA_01 | 4045 | 32.1 | 28.7 | 4.5 | 49.98
2025-06-14 19:10:00 | SPV_ALPHA_01 | 2198 | 17.3 | 27.9 | 3.2 | 50.02
2025-06-14 19:15:00 | SPV_ALPHA_01 | 0 | 0 | 28.2 | 3 | 50.04
2025-06-14 19:20:00 | SPV_ALPHA_01 | 0 | 0 | 27.6 | 3.9 | 50.01
2025-06-14 19:25:00 | SPV_ALPHA_01 | 0 | 0 | 27.7 | 3.4 | 50.01
2025-06-14 19:30:00 | SPV_ALPHA_01 | 0 | 0 | 28.4 | 3.7 | 50.02
2025-06-14 19:35:00 | SPV_ALPHA_01 | 0 | 0 | 28.7 | 3.4 | 50.04
2025-06-14 19:40:00 | SPV_ALPHA_01 | 0 | 0 | 28.3 | 2.4 | 49.99
2025-06-14 19:45:00 | SPV_ALPHA_01 | 0 | 0 | 28.2 | 3.7 | 49.96
2025-06-14 19:50:00 | SPV_ALPHA_01 | 0 | 0 | 27.6 | 3.7 | 49.97
2025-06-14 19:55:00 | SPV_ALPHA_01 | 0 | 0 | 27.3 | 3.1 | 50.05
2025-06-14 20:00:00 | SPV_ALPHA_01 | 0 | 0 | 28.1 | 4.2 | 50.03

## inverter_performance
date | plant_id | inverter_id | generation_kwh | pr_percent | status | specific_yield_kwh_kwp | availability_percent | deviation_from_fleet_avg_pct
2025-06-01 | SPV_ALPHA_01 | INV_A01 | 37814 | 70.21 | Normal | 3.37 | 99.5 | -5.2
2025-06-01 | SPV_ALPHA_01 | INV_A02 | 39753 | 73.81 | Normal | 3.55 | 99.4 | -0.4
2025-06-01 | SPV_ALPHA_01 | INV_A03 | 42031 | 78.04 | Normal | 3.75 | 98 | 5.3
2025-06-01 | SPV_ALPHA_01 | INV_A04 | 36591 | 67.94 | Normal | 3.26 | 99.9 | -8.3
2025-06-01 | SPV_ALPHA_01 | INV_B01 | 36812 | 68.35 | Normal | 3.28 | 99.9 | -7.8
2025-06-01 | SPV_ALPHA_01 | INV_B02 | 43011 | 79.86 | Normal | 3.84 | 99.2 | 7.8
2025-06-01 | SPV_ALPHA_01 | INV_B03 | 44045 | 81.78 | Normal | 3.93 | 99.9 | 10.4
2025-06-01 | SPV_ALPHA_01 | INV_B04 | 42532 | 78.97 | Normal | 3.79 | 98.1 | 6.6
2025-06-01 | SPV_ALPHA_01 | INV_C01 | 42413 | 78.75 | Normal | 3.78 | 97 | 6.3
2025-06-01 | SPV_ALPHA_01 | INV_C02 | 40227 | 74.69 | Normal | 3.59 | 98.4 | 0.8
2025-06-01 | SPV_ALPHA_01 | INV_C03 | 41401 | 76.87 | Normal | 3.69 | 99 | 3.7
2025-06-01 | SPV_ALPHA_01 | INV_C04 | 40636 | 75.45 | Normal | 3.62 | 99.5 | 1.8
2025-06-02 | SPV_ALPHA_01 | INV_A01 | 49647 | 89.94 | Normal | 4.43 | 97.3 | 8.5
2025-06-02 | SPV_ALPHA_01 | INV_A02 | 43409 | 78.64 | Normal | 3.87 | 97.1 | -5.1
2025-06-02 | SPV_ALPHA_01 | INV_A03 | 49156 | 89.05 | Normal | 4.38 | 98.7 | 7.4
2025-06-02 | SPV_ALPHA_01 | INV_A04 | 49426 | 89.54 | Normal | 4.41 | 97.7 | 8
2025-06-02 | SPV_ALPHA_01 | INV_B01 | 41902 | 75.91 | Normal | 3.74 | 99.5 | -8.4
2025-06-02 | SPV_ALPHA_01 | INV_B02 | 49376 | 89.45 | Normal | 4.4 | 97.9 | 7.9
2025-06-02 | SPV_ALPHA_01 | INV_B03 | 44949 | 81.43 | Normal | 4.01 | 97.4 | -1.8
2025-06-02 | SPV_ALPHA_01 | INV_B04 | 49702 | 90.04 | Normal | 4.43 | 97.9 | 8.6
2025-06-02 | SPV_ALPHA_01 | INV_C01 | 45695 | 82.78 | Normal | 4.08 | 97.3 | -0.1
2025-06-02 | SPV_ALPHA_01 | INV_C02 | 49183 | 89.1 | Normal | 4.39 | 97.4 | 7.5
2025-06-02 | SPV_ALPHA_01 | INV_C03 | 45352 | 82.16 | Normal | 4.04 | 99 | -0.9
2025-06-02 | SPV_ALPHA_01 | INV_C04 | 47908 | 86.79 | Normal | 4.27 | 99.8 | 4.7
2025-06-03 | SPV_ALPHA_01 | INV_A01 | 39537 | 73.41 | Normal | 3.53 | 99.2 | -1.7
2025-06-03 | SPV_ALPHA_01 | INV_A02 | 37254 | 69.17 | Normal | 3.32 | 98.2 | -7.4
2025-06-03 | SPV_ALPHA_01 | INV_A03 | 36774 | 68.28 | Normal | 3.28 | 98.5 | -8.6
2025-06-03 | SPV_ALPHA_01 | INV_A04 | 39440 | 73.23 | Normal | 3.52 | 99.9 | -2
2025-06-03 | SPV_ALPHA_01 | INV_B01 | 36204 | 67.22 | Normal | 3.23 | 98.1 | -10
2025-06-03 | SPV_ALPHA_01 | INV_B02 | 39742 | 73.79 | Normal | 3.54 | 99.9 | -1.2
2025-06-03 | SPV_ALPHA_01 | INV_B03 | 43297 | 80.39 | Normal | 3.86 | 97.3 | 7.6
2025-06-03 | SPV_ALPHA_01 | INV_B04 | 41832 | 77.67 | Normal | 3.73 | 98.6 | 4
2025-06-03 | SPV_ALPHA_01 | INV_C01 | 44352 | 82.35 | Normal | 3.96 | 98.1 | 10.2
2025-06-03 | SPV_ALPHA_01 | INV_C02 | 39354 | 73.07 | Normal | 3.51 | 97.6 | -2.2
2025-06-03 | SPV_ALPHA_01 | INV_C03 | 36974 | 68.65 | Normal | 3.3 | 99.5 | -8.1
2025-06-03 | SPV_ALPHA_01 | INV_C04 | 39844 | 73.98 | Normal | 3.55 | 99 | -1
2025-06-04 | SPV_ALPHA_01 | INV_A01 | 29978 | 87.87 | Normal | 2.67 | 98.8 | 2.7
2025-06-04 | SPV_ALPHA_01 | INV_A02 | 26591 | 77.94 | Normal | 2.37 | 99.4 | -8.9
2025-06-04 | SPV_ALPHA_01 | INV_A03 | 27805 | 81.5 | Normal | 2.48 | 97.4 | -4.8
2025-06-04 | SPV_ALPHA_01 | INV_A04 | 29555 | 86.63 | Normal | 2.64 | 97.2 | 1.2
2025-06-04 | SPV_ALPHA_01 | INV_B01 | 30650 | 89.84 | Normal | 2.73 | 97.6 | 5
2025-06-04 | SPV_ALPHA_01 | INV_B02 | 27655 | 81.06 | Normal | 2.47 | 99.6 | -5.3
2025-06-04 | SPV_ALPHA_01 | INV_B03 | 28269 | 82.86 | Normal | 2.52 | 97.4 | -3.2
2025-06-04 | SPV_ALPHA_01 | INV_B04 | 31391 | 92.01 | Normal | 2.8 | 97 | 7.5
2025-06-04 | SPV_ALPHA_01 | INV_C01 | 31159 | 91.33 | Normal | 2.78 | 97.4 | 6.7
2025-06-04 | SPV_ALPHA_01 | INV_C02 | 27184 | 79.68 | Normal | 2.42 | 97.8 | -6.9
2025-06-04 | SPV_ALPHA_01 | INV_C03 | 27426 | 80.39 | Normal | 2.45 | 99 | -6.1
2025-06-04 | SPV_ALPHA_01 | INV_C04 | 26614 | 78.01 | Normal | 2.37 | 97 | -8.9
2025-06-05 | SPV_ALPHA_01 | INV_A01 | 48874 | 70.44 | Normal | 4.36 | 97.7 | 7.1
2025-06-05 | SPV_ALPHA_01 | INV_A02 | 43698 | 62.98 | Normal | 3.9 | 97.5 | -4.3
2025-06-05 | SPV_ALPHA_01 | INV_A03 | 40686 | 58.64 | Normal | 3.63 | 99.2 | -10.9
2025-06-05 | SPV_ALPHA_01 | INV_A04 | 45946 | 66.22 | Normal | 4.1 | 99.2 | 0.6
2025-06-05 | SPV_ALPHA_01 | INV_B01 | 45391 | 65.42 | Normal | 4.05 | 99.3 | -0.6
2025-06-05 | SPV_ALPHA_01 | INV_B02 | 45800 | 66.01 | Normal | 4.08 | 97.3 | 0.3
2025-06-05 | SPV_ALPHA_01 | INV_B03 | 45696 | 65.86 | Normal | 4.08 | 99.8 | 0.1
2025-06-05 | SPV_ALPHA_01 | INV_B04 | 40582 | 58.49 | Normal | 3.62 | 99.3 | -11.1
2025-06-05 | SPV_ALPHA_01 | INV_C01 | 49727 | 71.67 | Normal | 4.43 | 98.6 | 8.9
2025-06-05 | SPV_ALPHA_01 | INV_C02 | 45189 | 65.13 | Normal | 4.03 | 99.9 | -1
2025-06-05 | SPV_ALPHA_01 | INV_C03 | 40777 | 58.77 | Normal | 3.64 | 98.4 | -10.7
2025-06-05 | SPV_ALPHA_01 | INV_C04 | 44565 | 64.23 | Normal | 3.97 | 99.1 | -2.4
2025-06-06 | SPV_ALPHA_01 | INV_A01 | 47114 | 74.04 | Normal | 4.2 | 99.7 | -0.2
2025-06-06 | SPV_ALPHA_01 | INV_A02 | 42876 | 67.38 | Normal | 3.82 | 97.2 | -9.2
2025-06-06 | SPV_ALPHA_01 | INV_A03 | 48317 | 75.93 | Normal | 4.31 | 97.2 | 2.3
2025-06-06 | SPV_ALPHA_01 | INV_A04 | 44925 | 70.6 | Normal | 4.01 | 98.9 | -4.9
2025-06-06 | SPV_ALPHA_01 | INV_B01 | 47706 | 74.97 | Normal | 4.25 | 98 | 1
2025-06-06 | SPV_ALPHA_01 | INV_B02 | 52249 | 82.11 | Normal | 4.66 | 98.6 | 10.7
2025-06-06 | SPV_ALPHA_01 | INV_B03 | 46745 | 73.46 | Normal | 4.17 | 98.8 | -1
2025-06-06 | SPV_ALPHA_01 | INV_B04 | 43137 | 67.79 | Normal | 3.85 | 99.1 | -8.6
2025-06-06 | SPV_ALPHA_01 | INV_C01 | 50805 | 79.84 | Normal | 4.53 | 99 | 7.6
2025-06-06 | SPV_ALPHA_01 | INV_C02 | 49952 | 78.5 | Normal | 4.46 | 99.2 | 5.8
2025-06-06 | SPV_ALPHA_01 | INV_C03 | 44314 | 69.64 | Normal | 3.95 | 98.4 | -6.1
2025-06-06 | SPV_ALPHA_01 | INV_C04 | 44454 | 69.86 | Normal | 3.96 | 98 | -5.8
2025-06-07 | SPV_ALPHA_01 | INV_A01 | 48374 | 74.56 | Normal | 4.31 | 98.2 | -1
2025-06-07 | SPV_ALPHA_01 | INV_A02 | 44650 | 68.82 | Normal | 3.98 | 98.3 | -8.6
2025-06-07 | SPV_ALPHA_01 | INV_A03 | 50567 | 77.94 | Normal | 4.51 | 98.1 | 3.5
2025-06-07 | SPV_ALPHA_01 | INV_A04 | 45247 | 69.74 | Normal | 4.04 | 99.8 | -7.4
2025-06-07 | SPV_ALPHA_01 | INV_B01 | 44358 | 68.37 | Normal | 3.96 | 99.5 | -9.2
2025-06-07 | SPV_ALPHA_01 | INV_B02 | 44630 | 68.79 | Normal | 3.98 | 97.3 | -8.6
2025-06-07 | SPV_ALPHA_01 | INV_B03 | 51332 | 79.12 | Normal | 4.58 | 99.4 | 5.1
2025-06-07 | SPV_ALPHA_01 | INV_B04 | 49438 | 76.2 | Normal | 4.41 | 98.8 | 1.2
2025-06-07 | SPV_ALPHA_01 | INV_C01 | 49496 | 76.29 | Normal | 4.41 | 98 | 1.3
2025-06-07 | SPV_ALPHA_01 | INV_C02 | 44935 | 69.26 | Normal | 4.01 | 98.1 | -8
2025-06-07 | SPV_ALPHA_01 | INV_C03 | 50573 | 77.95 | Normal | 4.51 | 99.3 | 3.5
2025-06-07 | SPV_ALPHA_01 | INV_C04 | 52675 | 81.19 | Normal | 4.7 | 99.2 | 7.8
2025-06-08 | SPV_ALPHA_01 | INV_A01 | 52364 | 82.29 | Normal | 4.67 | 98.8 | 10
2025-06-08 | SPV_ALPHA_01 | INV_A02 | 46090 | 72.43 | Normal | 4.11 | 98.7 | -3.2
2025-06-08 | SPV_ALPHA_01 | INV_A03 | 44671 | 70.2 | Normal | 3.98 | 99 | -6.1
2025-06-08 | SPV_ALPHA_01 | INV_A04 | 44792 | 70.39 | Normal | 3.99 | 97.3 | -5.9
2025-06-08 | SPV_ALPHA_01 | INV_B01 | 51117 | 80.33 | Normal | 4.56 | 98.1 | 7.4
2025-06-08 | SPV_ALPHA_01 | INV_B02 | 50270 | 79 | Normal | 4.48 | 98.7 | 5.6
2025-06-08 | SPV_ALPHA_01 | INV_B03 | 50728 | 79.72 | Normal | 4.52 | 99.5 | 6.6
2025-06-08 | SPV_ALPHA_01 | INV_B04 | 52428 | 82.39 | Normal | 4.68 | 99.5 | 10.1
2025-06-08 | SPV_ALPHA_01 | INV_C01 | 48756 | 76.62 | Normal | 4.35 | 98.9 | 2.4
2025-06-08 | SPV_ALPHA_01 | INV_C02 | 42774 | 67.22 | Normal | 3.81 | 99.8 | -10.1
2025-06-08 | SPV_ALPHA_01 | INV_C03 | 50951 | 80.07 | Normal | 4.54 | 97.8 | 7
2025-06-08 | SPV_ALPHA_01 | INV_C04 | 44346 | 69.69 | Normal | 3.96 | 99.1 | -6.8
2025-06-09 | SPV_ALPHA_01 | INV_A01 | 46109 | 66.64 | Normal | 4.11 | 98 | -4.4
2025-06-09 | SPV_ALPHA_01 | INV_A02 | 42760 | 61.8 | Normal | 3.81 | 99.6 | -11.3
2025-06-09 | SPV_ALPHA_01 | INV_A03 | 48960 | 70.76 | Normal | 4.37 | 98.2 | 1.5
2025-06-09 | SPV_ALPHA_01 | INV_A04 | 44262 | 63.97 | Normal | 3.95 | 98.9 | -8.2
2025-06-09 | SPV_ALPHA_01 | INV_B01 | 43030 | 62.19 | Normal | 3.84 | 99.2 | -10.8
2025-06-09 | SPV_ALPHA_01 | INV_B02 | 45071 | 65.14 | Normal | 4.02 | 98.3 | -6.5
2025-06-09 | SPV_ALPHA_01 | INV_B03 | 46462 | 67.15 | Normal | 4.14 | 98.1 | -3.7
2025-06-09 | SPV_ALPHA_01 | INV_B04 | 50683 | 73.25 | Normal | 4.52 | 99.3 | 5.1
2025-06-09 | SPV_ALPHA_01 | INV_C01 | 48974 | 70.78 | Normal | 4.37 | 97.3 | 1.5
2025-06-09 | SPV_ALPHA_01 | INV_C02 | 43272 | 62.54 | Normal | 3.86 | 97.5 | -10.3
2025-06-09 | SPV_ALPHA_01 | INV_C03 | 49534 | 71.59 | Normal | 4.42 | 99 | 2.7
2025-06-09 | SPV_ALPHA_01 | INV_C04 | 45701 | 66.05 | Normal | 4.08 | 99 | -5.2
2025-06-10 | SPV_ALPHA_01 | INV_A01 | 42236 | 68.97 | Normal | 3.77 | 98.3 | -0.3
2025-06-10 | SPV_ALPHA_01 | INV_A02 | 40153 | 65.57 | Normal | 3.58 | 99.3 | -5.2
2025-06-10 | SPV_ALPHA_01 | INV_A03 | 38592 | 63.02 | Normal | 3.44 | 98.3 | -8.9
2025-06-10 | SPV_ALPHA_01 | INV_A04 | 40251 | 65.73 | Normal | 3.59 | 99 | -5
2025-06-10 | SPV_ALPHA_01 | INV_B01 | 42248 | 68.99 | Normal | 3.77 | 99 | -0.3
2025-06-10 | SPV_ALPHA_01 | INV_B02 | 37924 | 61.93 | Normal | 3.38 | 98.2 | -10.5
2025-06-10 | SPV_ALPHA_01 | INV_B03 | 43350 | 70.79 | Normal | 3.87 | 97 | 2.3
2025-06-10 | SPV_ALPHA_01 | INV_B04 | 40429 | 66.02 | Normal | 3.61 | 97.6 | -4.6
2025-06-10 | SPV_ALPHA_01 | INV_C01 | 38825 | 63.4 | Normal | 3.46 | 97.8 | -8.4
2025-06-10 | SPV_ALPHA_01 | INV_C02 | 40692 | 66.45 | Normal | 3.63 | 97 | -4
2025-06-10 | SPV_ALPHA_01 | INV_C03 | 44795 | 73.15 | Normal | 4 | 97.5 | 5.7
2025-06-10 | SPV_ALPHA_01 | INV_C04 | 41201 | 67.28 | Normal | 3.67 | 99.1 | -2.8
2025-06-11 | SPV_ALPHA_01 | INV_A01 | 36875 | 66 | Normal | 3.29 | 99.5 | 0
2025-06-11 | SPV_ALPHA_01 | INV_A02 | 39612 | 70.9 | Normal | 3.53 | 97.2 | 7.4
2025-06-11 | SPV_ALPHA_01 | INV_A03 | 40110 | 71.79 | Normal | 3.58 | 97.1 | 8.8
2025-06-11 | SPV_ALPHA_01 | INV_A04 | 32573 | 58.3 | Normal | 2.91 | 99.8 | -11.7
2025-06-11 | SPV_ALPHA_01 | INV_B01 | 40110 | 71.79 | Normal | 3.58 | 98.7 | 8.8
2025-06-11 | SPV_ALPHA_01 | INV_B02 | 37528 | 67.17 | Normal | 3.35 | 99.1 | 1.8
2025-06-11 | SPV_ALPHA_01 | INV_B03 | 36137 | 64.68 | Normal | 3.22 | 97.3 | -2
2025-06-11 | SPV_ALPHA_01 | INV_B04 | 32589 | 58.33 | Normal | 2.91 | 98 | -11.6
2025-06-11 | SPV_ALPHA_01 | INV_C01 | 39568 | 70.82 | Normal | 3.53 | 98.9 | 7.3
2025-06-11 | SPV_ALPHA_01 | INV_C02 | 39841 | 71.31 | Normal | 3.55 | 99.8 | 8
2025-06-11 | SPV_ALPHA_01 | INV_C03 | 33193 | 59.41 | Normal | 2.96 | 99.5 | -10
2025-06-11 | SPV_ALPHA_01 | INV_C04 | 34578 | 61.89 | Normal | 3.08 | 98.8 | -6.2
2025-06-12 | SPV_ALPHA_01 | INV_A01 | 28354 | 64.18 | Normal | 2.53 | 98.2 | 0.6
2025-06-12 | SPV_ALPHA_01 | INV_A02 | 26843 | 60.76 | Normal | 2.39 | 98 | -4.8
2025-06-12 | SPV_ALPHA_01 | INV_A03 | 27007 | 61.13 | Normal | 2.41 | 97.5 | -4.2
2025-06-12 | SPV_ALPHA_01 | INV_A04 | 28261 | 63.97 | Normal | 2.52 | 97.3 | 0.3
2025-06-12 | SPV_ALPHA_01 | INV_B01 | 28257 | 63.96 | Normal | 2.52 | 99.7 | 0.3
2025-06-12 | SPV_ALPHA_01 | INV_B02 | 27122 | 61.39 | Normal | 2.42 | 99.2 | -3.8
2025-06-12 | SPV_ALPHA_01 | INV_B03 | 30439 | 68.9 | Normal | 2.71 | 99.4 | 8
2025-06-12 | SPV_ALPHA_01 | INV_B04 | 26322 | 59.58 | Normal | 2.35 | 97.4 | -6.6
2025-06-12 | SPV_ALPHA_01 | INV_C01 | 26048 | 58.96 | Normal | 2.32 | 98.8 | -7.6
2025-06-12 | SPV_ALPHA_01 | INV_C02 | 30024 | 67.96 | Normal | 2.68 | 99 | 6.5
2025-06-12 | SPV_ALPHA_01 | INV_C03 | 25902 | 58.63 | Normal | 2.31 | 99.3 | -8.1
2025-06-12 | SPV_ALPHA_01 | INV_C04 | 28147 | 63.71 | Normal | 2.51 | 99.3 | -0.1
2025-06-13 | SPV_ALPHA_01 | INV_A01 | 35248 | 72.26 | Normal | 3.14 | 98.3 | 6.1
2025-06-13 | SPV_ALPHA_01 | INV_A02 | 36531 | 74.89 | Normal | 3.26 | 98.7 | 10
2025-06-13 | SPV_ALPHA_01 | INV_A03 | 34272 | 70.26 | Normal | 3.06 | 98.9 | 3.2
2025-06-13 | SPV_ALPHA_01 | INV_A04 | 36062 | 73.93 | Normal | 3.22 | 98.9 | 8.6
2025-06-13 | SPV_ALPHA_01 | INV_B01 | 30497 | 62.52 | Normal | 2.72 | 97.2 | -8.2
2025-06-13 | SPV_ALPHA_01 | INV_B02 | 32770 | 67.18 | Normal | 2.92 | 97.9 | -1.4
2025-06-13 | SPV_ALPHA_01 | INV_B03 | 31458 | 64.49 | Normal | 2.81 | 97.2 | -5.3
2025-06-13 | SPV_ALPHA_01 | INV_B04 | 33277 | 68.22 | Normal | 2.97 | 97.9 | 0.2
2025-06-13 | SPV_ALPHA_01 | INV_C01 | 32843 | 67.33 | Normal | 2.93 | 97.2 | -1.1
2025-06-13 | SPV_ALPHA_01 | INV_C02 | 35809 | 73.41 | Normal | 3.19 | 97.2 | 7.8
2025-06-13 | SPV_ALPHA_01 | INV_C03 | 36062 | 73.93 | Normal | 3.22 | 99.6 | 8.6
2025-06-13 | SPV_ALPHA_01 | INV_C04 | 34116 | 69.94 | Normal | 3.04 | 98.5 | 2.7
2025-06-14 | SPV_ALPHA_01 | INV_A01 | 29142 | 40.6 | Underperforming | 2.6 | 71.6 | -20.2
2025-06-14 | SPV_ALPHA_01 | INV_A02 | 32660 | 45.5 | Below Target | 2.91 | 98.7 | -10.6
2025-06-14 | SPV_ALPHA_01 | INV_A03 | 33392 | 46.52 | Below Target | 2.98 | 99.4 | -8.6
2025-06-14 | SPV_ALPHA_01 | INV_A04 | 33966 | 47.32 | Below Target | 3.03 | 99.7 | -7
2025-06-14 | SPV_ALPHA_01 | INV_B01 | 35193 | 49.03 | Below Target | 3.14 | 98.3 | -3.6
2025-06-14 | SPV_ALPHA_01 | INV_B02 | 35646 | 49.66 | Below Target | 3.18 | 99.4 | -2.4
2025-06-14 | SPV_ALPHA_01 | INV_B03 | 35646 | 49.66 | Below Target | 3.18 | 99 | -2.4
2025-06-14 | SPV_ALPHA_01 | INV_B04 | 35847 | 49.94 | Below Target | 3.2 | 98 | -1.8
2025-06-14 | SPV_ALPHA_01 | INV_C01 | 35875 | 49.98 | Below Target | 3.2 | 98.4 | -1.8
2025-06-14 | SPV_ALPHA_01 | INV_C02 | 36248 | 50.5 | Below Target | 3.23 | 97.5 | -0.7
2025-06-14 | SPV_ALPHA_01 | INV_C03 | 36751 | 51.2 | Below Target | 3.28 | 97.2 | 0.6
2025-06-14 | SPV_ALPHA_01 | INV_C04 | 37770 | 52.62 | Below Target | 3.37 | 97.3 | 3.4

## loss_events
date | plant_id | start_time | end_time | duration_min | loss_type | affected_equipment | estimated_loss_kwh | note | severity
2025-06-04 | SPV_ALPHA_01 | 06:00 | 19:00 | 780 | weather | All inverters | 125000 | Heavy cloud cover observed all day. GTI 3.56 kWh/m2 vs typical 5.5-6.5 kWh/m2 | Low
2025-06-05 | SPV_ALPHA_01 | 10:30 | 11:30 | 60 | weather | All inverters | 8200 | Partial cloud cover 10:30-11:30. GTI reduced by approximately 40% | Low
2025-06-09 | SPV_ALPHA_01 | 09:15 | 10:00 | 45 | inverter_trip | INV_A01 | 4100 | INV_A01 tripped at 09:15 due to over-temperature alarm. Auto-reset at 10:00. | Medium
2025-06-12 | SPV_ALPHA_01 | 13:00 | 14:30 | 90 | grid_curtailment | All inverters | 22500 | Grid operator curtailment instruction received. Resumed normal generation at 14:30. | High
2025-06-14 | SPV_ALPHA_01 | 14:10 | 15:48 | 98 | grid_curtailment | All inverters | 86000 |  | High
2025-06-14 | SPV_ALPHA_01 | 09:00 | 19:00 | 600 | inverter_underperformance | INV_A01, INV_A02 | 18500 | INV_A01 PR at 40.6% — significantly below fleet average of 50.88% | Medium

## historical_performance
date | plant_id | generation_kwh | gti_kwh_m2 | pr_percent | cuf_percent | expected_generation_kwh | total_loss_kwh | week_generation_kwh | mtd_generation_kwh | qtd_generation_kwh
2025-06-01 | SPV_ALPHA_01 | 534400 | 5.62 | 74.1 | 19.36 | 667656 | 133256 | 0 | 534400 | 25534400
2025-06-02 | SPV_ALPHA_01 | 612300 | 5.76 | 82.9 | 22.18 | 684288 | 71988 | 0 | 1146700 | 26146700
2025-06-03 | SPV_ALPHA_01 | 538400 | 5.62 | 74.7 | 19.51 | 667656 | 129256 | 0 | 1685100 | 26685100
2025-06-04 | SPV_ALPHA_01 | 390400 | 3.56 | 85.6 | 14.14 | 422928 | 32528 | 0 | 2075500 | 27075500
2025-06-05 | SPV_ALPHA_01 | 610800 | 7.24 | 65.8 | 22.13 | 860112 | 249312 | 0 | 2686300 | 27686300
2025-06-06 | SPV_ALPHA_01 | 633600 | 6.64 | 74.2 | 22.96 | 788832 | 155232 | 0 | 3319900 | 28319900
2025-06-07 | SPV_ALPHA_01 | 656900 | 6.77 | 75.3 | 23.8 | 804276 | 147376 | 0 | 3976800 | 28976800
2025-06-08 | SPV_ALPHA_01 | 639500 | 6.64 | 74.8 | 23.17 | 788832 | 149332 | 639500 | 4616300 | 29616300
2025-06-09 | SPV_ALPHA_01 | 647700 | 7.22 | 69.7 | 23.47 | 857736 | 210036 | 1287200 | 5264000 | 30264000
2025-06-10 | SPV_ALPHA_01 | 569800 | 6.39 | 69.2 | 20.64 | 759132 | 189332 | 1857000 | 5833800 | 30833800
2025-06-11 | SPV_ALPHA_01 | 494600 | 5.83 | 66 | 17.92 | 692604 | 198004 | 2351600 | 6328400 | 31328400
2025-06-12 | SPV_ALPHA_01 | 378500 | 4.61 | 63.8 | 13.71 | 547668 | 169168 | 2730100 | 6706900 | 31706900
2025-06-13 | SPV_ALPHA_01 | 444700 | 5.09 | 68.1 | 16.11 | 604692 | 159992 | 3174800 | 7151600 | 32151600
2025-06-14 | SPV_ALPHA_01 | 513700 | 7.49 | 50.88 | 18.61 | 889812 | 376112 | 3688500 | 7665300 | 32665300

## metric_dictionary
metric | full_name | formula | unit | good_range | poor_threshold | notes
PR | Performance Ratio | Generation (kWh) / (GTI (kWh/m2) × DC Capacity (MWp) × 1000) | % | 70-85% | <65% | Key quality metric. Independent of location. Target: 75%
CUF | Capacity Utilisation Factor | Generation (kWh) / (AC Capacity (kW) × 24) | % | 18-25% | <15% | Also called Plant Load Factor. Daily target: 22%
GTI | Global Tilted Irradiance | Irradiance (W/m2) × Time (hours) / 1000 | kWh/m2 | 5.0-8.0 | <3.0 | Solar energy available at panel surface
Specific Yield | Energy per unit DC capacity | Generation (kWh) / DC Capacity (kWp) | kWh/kWp | 3.5-5.0 | <3.0 | Normalised generation for cross-plant comparison
Outage Loss | Energy lost due to grid or plant outage | Expected Generation - Actual Generation during outage period | kWh | 0 | Any loss >5000 kWh needs investigation | Caused by grid curtailment, inverter trips, or communication failure
Environmental Loss | Energy lost due to temperature or soiling | Estimated from PR loss attributable to environmental factors | kWh | <5% of expected | N/A | Temperature above 25C reduces output by ~0.4% per degree C
Clipping Loss | Energy lost due to AC/DC inverter capacity limit | DC output exceeding AC inverter capacity | kWh | <3% of expected | N/A | Common on high irradiance days when DC generation exceeds AC limit
Data Availability | Percentage of expected data intervals received | Actual intervals received / Expected intervals × 100 | % | >98% | <95% | Low availability indicates monitoring or communication gaps
Deviation | Percentage deviation from target generation | (Actual Generation - Expected Generation) / Expected Generation × 100 | % | >-5% | <-15% | Negative value indicates underperformance vs target
INV PR | Inverter-level Performance Ratio | Inverter Generation / (GTI × Inverter DC Capacity) | % | Within 5% of fleet PR | More than 10% below fleet average | Flag inverters significantly below fleet average for inspection
Inv_Power | Total inverter output power at a given timestamp | Sum of all inverter AC power outputs | kW | Follows GTI curve | Sharp drop while GTI is high = plant-side issue | Compare Inv_Power trend vs GTI trend to diagnose weather vs plant issues
Expected Generation | Theoretical generation under actual irradiance | GTI (kWh/m2) × DC Capacity (kWp) × Reference PR (0.80) | kWh | N/A | N/A | Used to calculate total losses for the day